HORIZON 2020

The Framework Programme for Research and Innovation

Project acronym: procuRE

Grant Agreement Number: 963648

Project full title: Pre-commercial Procurement of Breakthrough Solutions for

100% Renewable Energy Supply in Buildings

Call identifier: H2020-LC-SC3-2020-Joint-Actions-1

TD2a – Challenge Brief Annex E

Reference Building – Office description

TABLE OF CONTENTS

1	Introduction	3

2	Resources and inputs	4

2.1	Resources and inputs provided	4

3	Building model and assumptions description	5

3.1	Building model	5

3.2	Envelope characteristics	6

3.3	Emission units	7

3.4	Schedules	8

3.4.1	Occupancy schedules	8

3.4.2	Appliances schedules	9

3.4.3	Lighting schedules	10

3.4.4	Heating and cooling system schedules	10

3.5	Infiltration	12

3.6	Ventilation	12

3.7	Service Hot Water (SHW) demand	12

LIST OF FIGURES

Figure 1 Reference office, building model	5

Figure 2 Reference office, building model with internal structure details	5

Figure 3 Reference office, occupancy schedules	8

Figure 4 Reference office, equipment schedules	9

Figure 5 Reference office, lighting schedules	10

Figure 6 Reference office, heating set point schedules	11

Figure 7 Reference office, cooling set point schedules	12

LIST OF TABLES

Table 1 General characteristics of the reference office	5

Table 2 Reference office, building envelope characteristics, European Continental climate	7

Table 3 Reference office, building envelope characteristics, Mediterranean climate	7

# Introduction

This document constitutes an annex to the RfT_TD2 Challenge Brief and contains the description of the office reference building.

This document aims at describing the reference building model used to represent a reference office and the assumptions made.

Most of the inputs used come from documents made available by U.S. Department of Energy (DOE) as better specified in the following sections.

The choice to consider, as inputs for the considered reference office, indications developed by an American institution is motivated by the fact that these inputs are well referenced and freely available on the web (references are present in the following sections). It is however important to underline here that the indications taken from DOE regard mainly inputs related to the geometry of the building (total floor area, number of floors, windows fraction) and to their usage (schedule of occupancy, use of appliances, use of lighting system, use of heating and cooling system, use of ventilation system, use of service hot water). All these parameters could be considered enough general and, therefore, used also to characterize a typical office building located in the European region.

On the contrary, indications about wall construction are more specific and varies also within Europe depending on the considered climatic zone.

To have a sufficient representativity (with respect to the scope of the project) of the variability of building envelope characteristics based on the considered location, two different reference climates are taken into account. One is the European Continental climate, where the space heating is the most important building thermal demand and the other is the Mediterranean climate, where space cooling is critical. For each climate, one city has been selected as reference location. Considering the variability of European climate and the origin of project partners, Nuremberg and Istanbul have been chosen as reference locations for respectively the European Continental and Mediterranean climate. The thermal characteristics of envelope components in these two locations (Nuremberg and Istanbul) are taken from indications given by project partners based in these cities. These thermal characteristics represent typical envelope characteristic of office buildings built around year 2010.

# Resources and inputs

This section summarizes the main sources used to define office reference buildings characteristics. In addition, a short description of the documents about office reference buildings made available to suppliers for their calculations is reported.

As stated in the Introduction, most of the inputs used come from documents made available by U.S. DOE, in this case for the reference office buildings.

Thermal characteristics (mainly thermal transmittance) of envelope components have been instead indicated by project partners based in the cities taken as reference for the two analysed climates (European Continental and Mediterranean climate). These indications are in compliance with respectively German and Turkish national standards.

The climatic data of the two reference cities (Nuremberg and Istanbul) are taken from Meteonorm software version 7.3. For each reference city, the climatic data are reported for the entire considered year with an hourly timeframe. The climatic files for these two locations are made available in .tm2 and .epw formats. These two formats are those commonly used by dynamic simulation software. In addition, for each reference location, hourly value for the entire year of ambient air temperature, relative humidity (percentage) and total horizontal radiation are summarized in a .csv file.

## Resources and inputs provided

The documents about reference buildings made available to suppliers for their calculations are:

For each reference building: a word document describing the reference building considered and its characteristics (this document).

For each reference building: a simplified excel file obtained starting from the ones made available by by U.S. DOE2 containing building model inputs.

For each reference building: an .idf file taken from2 representing one of the files used by the U.S. DOE to run simulations in EnergyPlus. This file can be eventually used as a base for the development of the needed building models. However, this .idf file cannot be directly used by the suppliers for their calculation without a revision of some inputs (e.g., envelope components construction, occupancy schedule, climatic data). In fact, inputs considered by suppliers for their calculations must be aligned with indications presented in this report.

A folder containing climatic data files of the two reference locations.

# Building model and assumptions description

## Building model

The building model used and described in the following represents a typical (reference) office building constructed around year 2004. The building model inputs are mainly taken from documents made available by U.S. Department of Energy (DOE)2. From this reference, the considered building is a three floors office building with a total floor area equal to 4,9822 m2. The building presents a rectangular shape as visible in Figure 1 and Figure 2. Table 1, instead, summarizes other general characteristics of the analysed building.

Figure 1 Reference office, building model

Figure 2 Reference office, building model with internal structure details

Table 1 General characteristics of the reference office

| Quantity | Value | Unit |
| --- | --- | --- |
| Total floor area | 4 982 | m2 |
| Number of floors | 3 | - |
| Windows fraction (Windows to Wall Ratio) south | 0.33 | - |
| Windows fraction (Windows to Wall Ratio) east | 0.33 | - |
| Windows fraction (Windows to Wall Ratio) north | 0.33 | - |
| Windows fraction (Windows to Wall Ratio) west | 0.33 | - |
| Windows fraction (Windows to Wall Ratio) total | 0.33 | - |
| S/V ratio | 0.39 | - |
| Shading geometry | None | - |
| Azimuth | 0 | ° |
| Floor to ceiling height | 2.7 | m |
| Roof type | Flat roof | - |
| External wall total area (Gross dimensions) | 1 978 | m2 |
| External wall total area (Net dimensions) | 1 325 | m2 |
| Roof total area (Gross dimensions) | 1661 | m2 |
| Roof total area (Net dimensions) | 1661 | m2 |
| Windows dimensions south | 195.9 | m2 |
| Windows dimensions east | 130.6 | m2 |
| Windows dimensions north | 195.9 | m2 |
| Windows dimensions west | 130.6 | m2 |
| Windows total area | 652.8 | m2 |

## Envelope characteristics

One of the features that mostly influence thermal behaviour of a building are the envelope thermal characteristics. Wall construction, and therefore thermal characteristics are different for different climates and different periods of construction. In this work the focus is put on two climates, one is the European Continental climate and the other the Mediterranean one and on buildings constructed around year 2010.

For the European Continental climate, the city of Nuremberg has been selected as reference location and, therefore, indications about thermal characteristics of the envelope components (in particular, thermal transmittance) are taken from German Energy Savings Ordinance related to the period of construction considered3. The considered thermal transmittance values are those indicated in the standard for the reference building. For the Mediterranean climate, instead, the chosen reference city is Istanbul and indications about thermal characteristics of the envelope components (thermal transmittance) refer to existing office buildings and are in compliance with TS825-20084.

In the following Table 2 and Table 3, thermal characteristics of the main envelope components (opaque and transparent components) of the considered reference building respectively in the European Continental and Mediterranean climate are summarized.

Table 2 Reference office, building envelope characteristics, European Continental climate

| Quantity | Value | Unit |
| --- | --- | --- |
| Ground floor thermal transmittance | 0.35 | W/(m2.K) |
| External wall thermal transmittance | 0.28 | W/(m2.K) |
| External roof thermal transmittance | 0.20 | W/(m2.K) |
| Windows global thermal transmittance | 1.30 | W/(m2.K) |
| Windows solar thermal transmittance (g value) | 0.60 | W/(m2.K) |

Table 3 Reference office, building envelope characteristics, Mediterranean climate

| Quantity | Value | Unit |
| --- | --- | --- |
| Ground floor thermal transmittance | 0.55 | W/(m2.K) |
| External wall thermal transmittance | 0.56 | W/(m2.K) |
| External roof thermal transmittance | 0.37 | W/(m2.K) |
| Windows global thermal transmittance | 2.2 | W/(m2.K) |
| Windows solar thermal transmittance (g value) | 0.75 | W/(m2.K) |

## Emission units

Any specific indication is given in the document describing the commercial reference building models made available by U.S. DOE about the emission units to be considered. However, as a general indication it could be assumed for the reference office located in European Continental climate, where the focus is put on the coverage of space heating demand, that radiators are the most widely adopted solution. On the contrary, in hotter climates as the Mediterranean one, where space cooling demand is critical, the emission units generally adopted are fan coils.

## Schedules

### Occupancy schedules

According to the document describing the commercial reference building models made available by U.S. DOE2 the floor area per occupant index for a typical office result equal to 18-20 m2/pers. To define the number of occupants instantaneously present in the considered building, the previous value must be firstly multiplied by the area of the considered building and then by the occupancy schedule of the considered building. The office occupancy schedule for a typical day is reported in Figure 3. As can be noted, three different schedules for weekdays (blue columns), Saturdays (red columns) and other days (brown columns) are foreseen. The occupancy schedule during weekdays considers presence of occupants from 7 AM to 12 PM with a peak of occupancy in the typical office hours (from 9 AM to 5 PM with a decrement at noon). On the other hand, the occupancy schedule during a typical Saturday foresees a reduced presence of occupants with respect to a typical weekday from 7 AM to 5 PM. No presence of occupants is instead considered in any hour of other days.

Figure 3 Reference office, occupancy schedules

Finally, the contribution to building energy balance associated to the presence of occupants inside the building can be calculated by multiplying the number of people instantaneously present in the building by the nominal heat contribution of one person. The nominal heat contribution of one person depends on the activity performed. For the considered case this value has been assumed equal to 126 W/person according to indication from ASHRAE.

### Appliances schedules

The appliances schedules for the reference office considered are taken from the document describing the commercial reference building models made available by U.S. DOE8. Different appliances schedules are reported in Figure 4 for a typical weekday (blue columns), for a typical Saturday (yellow columns) and a typical day different from weekdays and Saturdays (brown columns). As can be noted from Figure 4 the peak energy consumption associated to appliances occurs between 9 AM and 5 PM during weekdays. A lower consumption by appliances occurs instead during Saturday until 2 PM In addition to that, from Figure 4 it can be noted that there is a base consumption due to appliances, equal to 40% (during weekdays) and 30% (during Saturdays and other days) of the nominal one outside hours characterized by presence of occupants in the office.

Figure 4 Reference office, equipment schedules

The contribution to building energy balance associated to the appliances present in the building can be calculated multiplying instantaneous value of equipment schedule by the nominal heat contribution due to appliances. From the document describing the commercial reference building models made available by U.S. DOE8 the nominal power of appliances for this kind of building is equal to 10.76 W/m2.

### Lighting schedules

The lighting schedules for the considered reference office building are also taken from the document describing the commercial reference building models made available by U.S. DOE8. Figure 5 reports the lighting schedules for a typical weekday (blue columns), for a typical Saturday (red columns) and for a typical day different from weekday and Saturday (brown columns). As can be noted from Figure 5 the peak consumption due to lighting system occurs between 9 AM and 5 PM of weekdays, hence, during the typical hours with presence of occupants in the office. A lower lighting system usage occurs from 6 AM to 9 AM and from 6 PM to 11 PM during weekdays and from 7 AM to 5 PM during Saturday. In addition to that, it is important to note that there is a base lighting system consumption, constant along the year, and equal to around 5% of the nominal lighting power.

Figure 5 Reference office, lighting schedules

The contribution to building energy balance associated to the presence of lighting system can be calculated multiplying instantaneous value of lighting schedule by the nominal heat contribution due to lighting system. From the document describing the commercial reference building models made available by U.S. DOE8 the nominal power of lighting system, for the considered building results equal to 10.76 W/m2.

### Heating and cooling system schedules

The heating and cooling set point schedules represent important variables that affect building heating and cooling demands. In this work, following indications made available by DOE for this kind of building8, different heating and cooling set point schedules are considered for different hours of the day and different days of the week. As can be seen in Figure 6 and Figure 7, there are three different heating (Figure 6) or cooling (Figure 7) set point schedules profiles, one for the weekdays (blue columns), one for Saturday, (red columns) and one for other days (yellow columns). The three heating set point schedules are shortly described in the following:

During the weekdays the temperature in the offices is maintained at 21°C from 7 AM to 10 PM while for the rest of the hours the set point temperature is decreased to 16°C.

During Saturday, the offices’ temperature is maintained at 21°C from 7 AM to 6 PM and at 16°C for the rest of the day.

In the other days, the heating set point temperature is always equal to 16°C.

Figure 6 Reference office, heating set point schedules

Regarding instead the three cooling set point schedules, in the following a short description is reported:

During the weekdays the offices’ temperature is maintained at 24°C from 7 AM to 10 PM while for the rest of the hours the set point temperature is equal to 27°C.

During Saturday, the offices’ cooling set point temperature is equal to 24°C from 7 AM to 7 PM while it is equal to 27°C for the rest of the day.

In the other days, the cooling set point temperature is always equal to 27°C.

Figure 7 Reference office, cooling set point schedules

## Infiltration

According to indications contained in the document describing the commercial reference building models made available by U.S. DOE8 a peak infiltration air change rate equal to around 0.2 vol/h is considered. In addition, an infiltration schedule is assumed to decrease (becoming 25% of the peak value) the infiltration air change rate when the HVAC system is enabled, and the building is pressurized. The HVAC system is considered in operation from 7 AM to 10 PM during the weekdays and from 7 AM to 6 PM during Saturdays. As result, the infiltration rate is decreased to 0.05 vol/h when HVAC system is in operation, while it is equal to 0.2 vol/h when HVAC system is disabled (during night, on Sundays and holidays).

## Ventilation

Indications about ventilation air change rate are taken from the document describing the commercial reference building models made available by U.S. DOE8. In this document the prescribed ventilation air change rate per unit floor area for the reference office results equal to 0.51 l/s.m2. In the same document any comment about the presence of a mechanical ventilation system with eventually the possibility to exploit heat recovery is mentioned.

## Service Hot Water (SHW) demand

The reference office presents a Service Hot Water (SHW) demand very limited. According to the document describing the commercial reference building models made available by U.S. DOE8 the annual SHW consumption of the building is equal to 174.6 m3, while the peak SHW demand is equal to 37.5 l/h. The temperature at which SHW is produced is 60°C, while the temperature of the SWH at user side is decreased to 43°C.

https://www.energy.gov/eere/buildings/new-construction-commercial-reference-buildings

refbldg_mediumoffice_new2004_v1.3_5.0.zip available at: https://www.energy.gov/eere/downloads/reference-buildings-building-type-medium-office

German Energy Savings Ordinance (EnEv 2009). Indication for the reference building specified in Annex 2, table 1. https://enev-online.org/enev_2009_volltext/index.htm

TS825-2008 “Thermal insulation requirements for buildings“ http://www1.mmo.org.tr/resimler/dosya_ekler/cf3e258fbdf3eb7_ek.pdf

Meteonorm software: https://meteonorm.com/en/

S (gross building dispersing surface) calculated as the sum of (Gross dimensions) total area of external walls (windows area included), roof and ground floor. V (conditioned gross building volume). Both inputs (S and V) are taken from documents made available by U.S. DOE2

Windows area included

U.S. Department of Energy Commercial Reference Building Models of the National Building Stock, https://www.nrel.gov/docs/fy11osti/46861.pdf

Typical metabolic heat generation for standing relaxed activity. Source: Ashrae handbook of fundamentals 2009. Table 4. pag. 9-6