HORIZON 2020

The Framework Programme for Research and Innovation

Project acronym: procuRE

Grant Agreement Number: 963648

Project full title: Pre-commercial Procurement of Breakthrough Solutions for

100% Renewable Energy Supply in Buildings

Call identifier: H2020-LC-SC3-2020-Joint-Actions-1

TD2a – Challenge Brief Annex E

Reference Building - School description

TABLE OF CONTENTS

1	Introduction	3

2	Resources and other inputs	4

2.1	Resources and inputs provided	4

3	Building model and assumptions description	5

3.1	Building model	5

3.2	Envelope characteristics	6

3.3	Emission units	7

3.4	Schedules	7

3.4.1	Occupancy schedules	7

3.4.2	Appliances’ schedules	9

3.4.3	Lighting schedules	10

3.4.4	Heating and cooling system schedules	11

3.5	Infiltration	13

3.6	Ventilation	13

3.7	Service Hot Water (SHW) demand	13

LIST OF FIGURES

Figure 1 Secondary school, building model	5

Figure 2 Secondary school, classroom occupancy schedules from EN 16798-1:2019	8

Figure 3 Secondary school, office occupancy schedules	9

Figure 4 Secondary school, equipment schedules	10

Figure 5 Secondary school, lighting schedules	11

Figure 6 Secondary school, heating set point schedules	12

Figure 7 Secondary school, cooling set point schedules	13

LIST OF TABLES

Table 1 General characteristics of the reference secondary school	5

Table 2 Reference school, building envelope characteristics, European Continental climate	7

Table 3 Reference school, building envelope characteristics, Mediterranean climate	7

# Introduction

This document constitutes an annex to the RfT_TD2 Challenge Brief and contains the description of the school reference building.

This document aims at describing the reference building model used to represent a reference school and the assumptions made.

Most of the inputs used come from documents made available by U.S. Department of Energy (DOE) as better specified in the following sections.

The choice to consider, as inputs for the considered reference school, indications developed by an American institution is motivated by the fact that these inputs are well referenced and freely available on the web (references are present in the following sections). It is however important to underline here that the indications taken from DOE regard mainly inputs related to the geometry of the building (total floor area, number of floors, windows fraction) and to their usage (use of appliances, use of lighting system, use of heating and cooling system, use of ventilation system, use of service hot water). All these parameters could be considered enough general and, therefore, used also to characterize a typical school located in the European region.

On the contrary, indications about wall construction are more specific and varies also within Europe depending on the considered climatic zone.

To have a sufficient representativity (with respect to the scope of the project) of the variability of building envelope characteristics based on the considered location, two different reference climates are taken into account. One is the European Continental climate, where the space heating is the most important building thermal demand and the other is the Mediterranean climate, where space cooling is critical. For each climate, one city has been selected as reference location. Considering the variability of European climate and the origin of project partners, Nuremberg and Istanbul have been chosen as reference locations for respectively the European Continental and Mediterranean climate. The thermal characteristics of envelope components in these two locations (Nuremberg and Istanbul) are taken from indications given by project partners based in these cities. These thermal characteristics represent typical envelope characteristic of schools built around year 2010.

# Resources and other inputs

This section summarizes the main sources used to define school reference buildings characteristics. In addition, a short description of the material about school reference buildings made available to suppliers for their calculations is reported.

As stated in the Introduction, most of the inputs used come from documents made available by U.S. DOE, in this case for the reference school buildings. In addition to that, occupancy schedules for classroom zones are taken from standard EN 16798-1:2019.

Thermal characteristics (mainly thermal transmittance) of envelope components have been instead indicated by project partners based in the cities taken as reference for the two analysed climates (European Continental and Mediterranean climate). These indications are in compliance with respectively German and Turkish national standards.

The climatic data of the two reference cities (Nuremberg and Istanbul) are taken from Meteonorm software version 7.3. For each reference city, the climatic data are reported for the entire considered year with an hourly timeframe. The climatic files for these two locations are made available in .tm2 and .epw formats. These two formats are those commonly used by dynamic simulation software. In addition, for each reference location, hourly value for the entire year of ambient air temperature, relative humidity (percentage) and total horizontal radiation are summarized in a .csv file.

## Resources and inputs provided

The documents about reference buildings made available to suppliers for their calculations are:

For each reference building: a word document describing the reference building considered and its characteristics (this document).

For each reference building: a simplified excel file obtained starting from the one made available by U.S. DOE2 containing building model inputs.

For each reference building: an .idf file taken from2 representing one of the files used by the U.S. DOE to run simulations in EnergyPlus. This file can be eventually used as a base for the development of the needed building models. However, this .idf file cannot be directly used by the suppliers for their calculation without a revision of some inputs (e.g., envelope components construction, occupancy schedule, climatic data). In fact, inputs considered by suppliers for their calculations must be aligned with indications presented in this report.

A folder containing climatic data files of the two reference locations.

# Building model and assumptions description

## Building model

The building model used and described in the following represents a typical (reference) secondary school constructed around year 2004. The building model inputs are mainly taken from documents made available by U.S. Department of Energy (DOE)2. From this reference, the considered building is a two floors secondary school with a total floor area equal to 19,592 m2. The building presents an “E” shape as visible in Figure 1. Table 1, instead, summarizes other general characteristics of the analysed building.

Figure 1 Secondary school, building model

Table 1 General characteristics of the reference secondary school

| Quantity | Value | Unit |
| --- | --- | --- |
| Total floor area | 19 592 | m2 |
| Number of floors | 2 | - |
| Windows fraction (Windows to Wall Ratio) south | 0.35 | - |
| Windows fraction (Windows to Wall Ratio) east | 0.35 | - |
| Windows fraction (Windows to Wall Ratio) north | 0.35 | - |
| Windows fraction (Windows to Wall Ratio) west | 0.28 | - |
| Windows fraction (Windows to Wall Ratio) total | 0.34 | - |
| S/V ratio | 0.32 | - |
| Shading geometry | None | - |
| Azimuth | 0 | ° |
| Floor to ceiling height | 4 | m |
| Roof type | flat roof | - |
| External wall total area (Gross dimensions) | 6 384.00 | m2 |
| External wall total area (Net dimensions) | 4 088.16 | m2 |
| Roof total area (Gross dimensions) | 11 902.00 | m2 |
| Roof total area (Net dimensions) | 11 768.70 | m2 |
| Windows dimensions south | 753.2 | m2 |
| Windows dimensions east | 291.6 | m2 |
| Windows dimensions north | 753.2 | m2 |
| Windows dimensions west | 291.2 | m2 |
| Windows total area | 2 089.2 | m2 |

Additional details on the various zones used in the building model can be found in the Excel file provided in the accompaniment material or in the documents from U.S. DOE2.

## Envelope characteristics

One of the features that mostly influence thermal behaviour of a building are the envelope thermal characteristics. Wall construction, and therefore thermal characteristics are different for different climates and different periods of construction. In this work the focus is put on two climates, one is the European Continental climate and the other the Mediterranean one and on buildings constructed around year 2010.

For the European Continental climate, the city of Nuremberg has been selected as reference location and, therefore, indications about thermal characteristics of the envelope components (in particular, thermal transmittance) are taken from German Energy Savings Ordinance related to the period of construction considered4. The considered thermal transmittance values are those indicated in the standard for the reference building. For the Mediterranean climate, instead, the chosen reference city is Istanbul and indications about thermal characteristics of the envelope components (thermal transmittance) refer to existing schools and are in compliance with TS825-20085.

In the following Table 2 and Table 3, thermal characteristics of the main envelope components (opaque and transparent components) of the considered reference building respectively in the European Continental and Mediterranean climate are summarized.

Table 2 Reference school, building envelope characteristics, European Continental climate

| Quantity | Value | Unit |
| --- | --- | --- |
| Ground floor thermal transmittance | 0.35 | W/(m2.K) |
| External wall thermal transmittance | 0.28 | W/(m2.K) |
| External roof thermal transmittance | 0.20 | W/(m2.K) |
| Windows global thermal transmittance | 1.30 | W/(m2.K) |
| Windows solar thermal transmittance (g value) | 0.60 | W/(m2.K) |

Table 3 Reference school, building envelope characteristics, Mediterranean climate

| Quantity | Value | Unit |
| --- | --- | --- |
| Ground floor thermal transmittance | 0.57 | W/(m2.K) |
| External wall thermal transmittance | 0.57 | W/(m2.K) |
| External roof thermal transmittance | 0.38 | W/(m2.K) |
| Windows global thermal transmittance | 2.2 | W/(m2.K) |
| Windows solar thermal transmittance (g value) | 0.75 | W/(m2.K) |

## Emission units

Any specific indication is given in the document describing the commercial reference building models made available by U.S. DOE about the emission units to be considered. However, as a general indication it could be assumed for the reference school located in European Continental climate, where the focus is put on the coverage of space heating demand, that radiators are the most widely adopted solution. On the contrary, in hotter climates as the Mediterranean one, where space cooling demand is critical, the emission units generally adopted are fan coils.

## Schedules

### Occupancy schedules

According to the document describing the commercial reference building models made available by U.S. DOE10 the floor area per occupant index for a typical classroom of the reference secondary school results equal to 4 m2/pers. To define the number of occupants instantaneously present in the considered classroom, the previous value must be firstly multiplied by the area of the considered classroom and then by the occupancy schedule of the considered building’s zone.

However, after discussions with procuRE partners, the occupancy schedule profiles suggested by U.S. DOE10 for a typical classroom are considered not enough representative of the occupancy schedule in a typical European school. For this reason, it has been decided to use, only for the occupancy schedule of classroom zone, not the input suggested by U.S. DOE10 but the occupancy schedule reported in standard EN 16798-1:20193. This profile is valid for the school days, while no occupants are foreseen for the rest of the time. The occupancy schedule considered in this work, taken from EN 16798-1:20193 is shown in Figure 2.

Figure 2 Secondary school, classroom occupancy schedules from EN 16798-1:20193

It has to be reported here that, generally, a secondary school contains not only classrooms for teaching activities but also zones of the building used as offices. For this reason, in the document describing the commercial reference building models made available by U.S. DOE10, also office occupancy profiles are included in the description of the reference secondary school. From the same document, the floor area per occupant index for a typical office of the reference secondary school results in the range 18-20 m2/pers. The number of occupants instantaneously present in the considered office is calculated, as previously, multiplying the floor area per occupant index by the area of the considered office (1064 m2 from10) and then by the occupancy schedule of the considered building’s zone. Figure 3 shows the office occupancy schedules for school year weekdays (blue columns) and for summer weekdays (yellow columns). As can be noted the occupants are mainly present in office from 9 AM to 5 PM with a reduced number of occupants present also until 9 PM during school year weekdays.

Figure 3 Secondary school, office occupancy schedules

In addition to classrooms and offices the document describing the commercial reference building models made available by U.S. DOE10 also reports occupancy schedule of other zones generally present in a secondary school characterized by specific occupancy schedules. The zones considered are the gym, the cafeteria and the auditorium. However, considering the limited area of gym, cafeteria and auditorium with respect to the building area used as classrooms and offices, and to avoid unnecessary complexity of the reference school model, these additional three building zones are not considered.

Finally, the contribution to building energy balance associated to the presence of occupants inside the building can be calculated multiplying the number of people instantaneously present in the building by the nominal heat contribution of one person. The nominal heat contribution of one person depends on the activity performed. For the considered case this value has been assumed equal to 126 W/pers according to indication from ASHRAE.

### Appliances’ schedules

The appliances’ schedules for the reference secondary school considered are taken from the document describing the commercial reference building models made available by U.S. DOE10. Different appliances schedules are reported in Figure 4 for a typical weekday during the school year (blue columns) and for a typical weekday during summer (yellow columns). Moreover, in the same figure also the appliances schedule for a typical weekend day during school year (red columns) and during summer (light blue columns) are reported. As can be noted from Figure 4 the peak consumption associated to appliances occurs between 9 AM and 5 PM during the school year. A lower appliances consumption occurs instead during weekdays in summer period in the same hours of the day. In addition to that, from Figure 4 it can be noted that there is a base consumption due to appliances, equal to around 35% and 25% of the nominal one respectively during school year and summer period.

Figure 4 Secondary school, equipment schedules

The contribution to building energy balance associated to the appliances present in the building can be calculated multiplying instantaneous value of equipment schedule by the nominal heat contribution due to appliances. From the document describing the commercial reference building models made available by U.S. DOE10 the nominal power of appliances is equal to 10 W/m2. This value is valid for both classrooms and office part of the building.

### Lighting schedules

The lighting schedules for the reference secondary school considered are also taken from the document describing the commercial reference building models made available by U.S. DOE10. Figure 5 reports the lighting schedules for a typical school year weekday (blue columns) and for a typical summer weekday (yellow columns). In addition, the same figure also shows the lighting schedules during a typical weekend day of the school year (red columns) and weekend day of the summer period (light blue). As can be noted from Figure 5 the peak consumption due to lighting system occurs between 8 AM and 9 PM during the school year. A lower lighting system usage occurs also during weekdays in summer period from 9 AM to 8 PM. Moreover, it is important to note that there is a base lighting system consumption, constant along the year, and equal to around 20% of the nominal lighting power.

Figure 5 Secondary school, lighting schedules

The contribution to building energy balance associated to the presence of lighting system can be calculated multiplying instantaneous value of lighting schedule by the nominal heat contribution due to lighting system. From the document describing the commercial reference building models made available by U.S. DOE10 the nominal power of lighting system results equal to 15 W/m2. As for appliances, also in this case, this nominal value is valid for both classrooms and office part of the building.

### Heating and cooling system schedules

The heating and cooling set point schedules represent important variables that affect building heating and cooling demands. In this work, following indications made available by DOE for this kind of building10, different heating and cooling set point schedules are considered for different hours of the day and different zones of the building. As can be seen in Figure 6 and Figure 7, there are three different heating (Figure 6) or cooling (Figure 7) set point schedules profiles, one for the weekdays (blue columns), one for the weekend days (also valid for holydays and summer period that is considered between June 30th and August 31st, red columns) and one for building’s zones not used as classrooms (e.g. restroom, yellow columns). The three heating set point schedules are shortly described in the following:

During the weekdays the classrooms and offices temperature is maintained at 21°C from 7 AM to 9 PM while for the rest of the hours the set point temperature is decreased to 16°C.

During the weekend days, holidays, and summer period the classrooms and offices temperature is maintained at 16°C for the entire day.

In zones of the building not used as classrooms or offices the heating set point temperature is always equal to 16°C.

Figure 6 Secondary school, heating set point schedules

Regarding instead the three cooling set point schedules in the following a short description is reported:

During the weekdays the classrooms and offices temperature is maintained at 24°C from 7 AM to 9 PM while for the rest of the hours the set point temperature is equal to 27°C.

During the weekend days, holidays, and summer period the classrooms and offices cooling set point temperature is always equal to 27°C for the entire day.

In zones of the building not used as classrooms or offices the cooling set point temperature is always equal to 27°C.

Figure 7 Secondary school, cooling set point schedules

## Infiltration

According to indications contained in the technical support document7 a peak infiltration air change rate equal to 0.5 vol/h is considered. In addition, an infiltration schedule is assumed to decrease (halve) the infiltration air change rate when the HVAC system is enabled, and the building is pressurized. The HVAC system is considered in operation from 8 AM to 9 PM during the weekdays. As result, the infiltration rate is decreased to 0.25 vol/h when HVAC system is in operation, while it is equal to 0.5 vol/h when HVAC system is disabled (during night and on weekends).

## Ventilation

Indications about ventilation air change rate are taken from the document describing the commercial reference building models made available by U.S. DOE10. In this document the prescribed ventilation air change rate per unit floor area for a classroom results equal to 1.77 l/(s.m2). Regarding instead the office zone eventually presents in the same building, the ventilation air change rate per unit floor area to be considered is equal to 0.51 l/(s.m2). In the document describing the commercial reference building models made available from U.S. DOE10 any comment about the presence of a mechanical ventilation system with eventually the possibility to exploit heat recovery is mentioned.

## Service Hot Water (SHW) demand

The reference secondary school presents a Service Hot Water (SHW) demand mainly related to the presence of the gym. According to the document describing the commercial reference building models made available by U.S. DOE10 the annual SHW consumption of the building is equal to 2678 m3, while the peak SHW demand is equal to 395 l/h. The temperature at which SHW is produced is 60°C, while the temperature of the SWH at user side is decreased to 43°C.

https://www.energy.gov/eere/buildings/new-construction-commercial-reference-buildings

refbldg_secondaryschool_new2004_v1.3_5.0.zip available at: https://www.energy.gov/eere/downloads/reference-buildings-building-type-secondary-school

EN 16798-1:2019 16798-1:2019 Energy performance of buildings - Ventilation for buildings - Part 1: Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics - Module M1-6

German Energy Savings Ordinance (EnEv 2009). Indication for the reference building specified in Annex 2, table 1. https://enev-online.org/enev_2009_volltext/index.htm

TS825-2008 “Thermal insulation requirements for buildings“ http://www1.mmo.org.tr/resimler/dosya_ekler/cf3e258fbdf3eb7_ek.pdf

Meteonorm software: https://meteonorm.com/en/

Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf

S (gross building dispersing surface) calculated as the sum of Gross dimensions – total area of external walls (windows area included), roof and ground floor. V (gross conditioned building volume). Both inputs (S and V) are taken from document made available by U.S. DOE2

Windows area included

U.S. Department of Energy Commercial Reference Building Models of the National Building Stock, https://www.nrel.gov/docs/fy11osti/46861.pdf

Typical metabolic heat generation for standing relaxed activity. Source: Ashrae handbook of fundamentals 2009. Table 4. pag. 9-6