## Legend
Colour legend:
Text in black | Original input from U.S. DOE
Text in red | Input available in the procuRE ref. buildings documents
Legend:
BLDG | Building
CLGSETP | Space cooling temperature set point
Corr | Corridor
ELEC | Electric
EQUIP | Equipment
FLR | Floor
HTGSETP | Space heating temperature set point
HVAC | Heating Ventilation Air Conditioning
INFIL | Infiltration
Mech | Mechanical room
MinOA | Minimum outside air requirement
OCC | Occupancy
SCH, SCHD, SCHED | Schedule
SWH | Service water heating
VELO | Velocity
WD | Weekdays
ZN | Zone
Note on B2: Trentin Federico: available at: https://www.energy.gov/eere/downloads/reference-buildings-building-type-secondary-school

## BuildingSummary
Building Summary Secondary School new construction
|  | Value | Data Source
Program
| Building Name | Secondary School Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
| Skylight/TDD Percentage | 1.12%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | flat roof | procuRE ref. buildings documents
Fabric
Exterior walls
| Construction Type | See procuRE ref. buildings documents | procuRE ref. buildings documents
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | See procuRE ref. buildings documents | procuRE ref. buildings documents
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, et al. 2007
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 133.8
| Operable area (m2) | 0
Foundation
| Foundation Type | -
| Construction | See procuRE ref. buildings documents | procuRE ref. buildings documents
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | -
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | -
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.16087 | See Reference Building Technical Report
HVAC
System Type
Heating Type
Cooling Type
Fan Control
Service Water Heating
SWH Type
Fuel
Thermal Efficiency (%)
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 2677.93

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.047735
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.07774
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.1503
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.10638
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 15.0695 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 15.0695 | 5 |  |  | 10 |  | 4160 |  | 0.066279
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 9.6875 | 5 |  |  | 8 |  | 7904 |  | 0.070501
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 12.9167 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.045349
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 15.0695 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.087209
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.31983
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.34983
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.42239
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.37847
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 13.9931 | 10 |  |  | 8 |  | 1544.8276 |  | 0.34854
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0.27209
Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
|  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69
|  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1457.54
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75 | 944.32
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13 | 628.36
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2176.29
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 22.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25 | 784.83
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82 | 14.1
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2 | 389.41
|  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.19 | 6.91
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_SCH | Temperature | Through 6/30 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296 | 67577.14
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
|  | Through 9/1 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 615
|  | Through 12/31 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
CLGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | SummerDesign | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603 | 0 | 0
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
HTGSETP_SCH | Temperature | Through 6/30 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768 | 40045.71
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
|  | Through 9/1 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 439
|  | Through 12/31 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
HTGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | WinterDesign | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459 | 0 | 0
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SHW_default Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
SHW_Kitchen Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600